## Summary
Public Service Company of New Mexico
Line | Load and Capacity Contribution at Summer Peak
No. | Description | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
(1) | Forecasted System Peak Demand | 1911.4279 | 1961.1432 | 2008.846 | 2055.6842 | 2107.5492 | 2154.4344 | 2189.4465 | 2218.5789 | 2248.5954 | 2279.6021 | 2311.545 | 2344.404 | 2378.1477 | 2412.813 | 2448.3158 | 2484.6586 | 2521.9116 | 2559.8905 | 2598.6829 | 2638.3528
(2) | Forecasted Incremental Energy Efficiency | -23.1481 | -36.3409 | -51.2761 | -62.8144 | -76.5794 | -89.2883 | -103.2105 | -113.2392 | -120.0379 | -129.2126 | -136.009 | -137.8068 | -145.5745 | -147.2487 | -141.8452 | -137.9661 | -134.8816 | -134.007 | -128.8298 | -122.2138
(3) | Forecasted Incremental Customer Sited PV | -17.6798 | -24.9022 | -31.5698 | -31.5698 | -31.5698 | -32.5461 | -33.5359 | -34.5397 | -35.5575 | -36.5895 | -37.636 | -38.6972 | -39.7732 | -40.8643 | -41.9706 | -43.0924 | -44.23 | -45.3834 | -46.5531 | -47.739
(4) | Net System Peak Demand (MW) | 1870.6 | 1899.9 | 1926 | 1961.3 | 1999.4 | 2032.6 | 2052.7 | 2070.8 | 2093 | 2113.8 | 2137.9 | 2167.9 | 2192.8 | 2224.7 | 2264.5 | 2303.6 | 2342.8 | 2380.5 | 2423.3 | 2468.4
(5) | Four Corners | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0
(6) | San Juan | 783 | 497 | 497 | 497 | 497 | 497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(7) | Total Coal Resources (MW) | 983 | 697 | 697 | 697 | 697 | 697 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0
(8) | Palo Verde Unit 1 & Unit 2 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268 | 268
(9) | Palo Verde Unit 3 | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
(10) | Total Nuclear Resources (MW) | 268 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402
(11) | Reeves | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
(12) | Afton | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
(13) | Lordsburg | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
(14) | Luna | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189
(15) | Rio Bravo | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
(16) | Valencia | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(17) | La Luz | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
(18) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 187 | 187 | 187
(19) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40
(20) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 187 | 187 | 187 | 187
(21) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
(22) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187
(23) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
(24) | Natural Gas Fired Resource (peaking) | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374
(25) | Total Natural Gas Resources (MW) | 981 | 981 | 981 | 981 | 981 | 981 | 1396 | 1396 | 1396 | 1396 | 1396 | 1433 | 1474 | 1474 | 1474 | 1701 | 1888 | 1888 | 1888 | 1888
(26) | Total Demand Response Programs (MW, Net of losses) | 45 | 46.5 | 48 | 49.4 | 51 | 52.5 | 54 | 55.5 | 57 | 58.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
(27) | 200 MW Wind Purchase (NMWEC) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(28) | 104 MW Wind Purchase (Red Mesa) | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 0
(29) | 0.5 MW Prosperity Battery Demo | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
(30) | Utility Scale Solar PV (22 MW - 2012 REPP) | 11.8311 | 11.7333 | 11.6356 | 11.6356 | 11.5378 | 11.5378 | 11.44 | 11.3422 | 11.3422 | 11.2444 | 11.2444 | 11.1467 | 11.1467 | 11.0489 | 10.9511 | 10.9511 | 10.8533 | 10.8533 | 10.7556 | 10.7556
(31) | Utility Scale Solar PV (20 MW - 2013 REPP) | 10.7907 | 10.7907 | 10.6977 | 10.6977 | 10.6047 | 10.6047 | 10.5116 | 10.4186 | 10.4186 | 10.3256 | 10.3256 | 10.2326 | 10.2326 | 10.1395 | 10.1395 | 10.0465 | 10.0465 | 9.9535 | 9.8605 | 9.8605
(32) | Utility Scale Solar PV (23 MW - 2014 REPP) | 15.5 | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 15.1 | 15 | 14.9 | 14.8 | 14.8 | 14.7 | 14.6 | 14.5 | 14.5 | 14.4 | 14.3 | 14.3 | 14.2 | 14.1
(33) | Utility Scale Solar PV (40 MW - 2015 REPP) | 30.2 | 29.9 | 29.7 | 29.5 | 29.3 | 29.1 | 28.8 | 28.6 | 28.4 | 28.2 | 28 | 27.8 | 27.6 | 27.4 | 27.1 | 26.9 | 26.7 | 26.5 | 26.3 | 26.1
(34) | PNM Sky Blue - 1.5 MW Solar | 0.8093 | 0.8093 | 0.80233 | 0.80233 | 0.79535 | 0.79535 | 0.78837 | 0.7814 | 0.7814 | 0.77442 | 0.77442 | 0.76744 | 0.76744 | 0.76047 | 0.76047 | 0.75349 | 0.75349 | 0.74651 | 0.73953 | 0.73953
(35) | Dale Burgett Geothermal Plant | 2.2 | 2.2 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 0 | 0 | 0
(36) | 400 MW Wind | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
(37) | 50 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
(38) | 100 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
(39) | 50 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
(40) | 100 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
(41) | 100 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
(42) | 100 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
(45) | 100 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
(46) | 50 MW Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.3 | 17.3 | 17.3
(47) | Data Center 1 Solar PV - 20 MW | 0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
(48) | Data Center 1 Solar PV - 40 MW | 0 | 0 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
(49) | Data Center 1 Solar PV - 30 MW | 0 | 0 | 0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
(50) | Data Center 1 Solar PV - 30 MW | 0 | 0 | 0 | 0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
(51) | Data Center 1 Solar PV - 40 MW | 0 | 0 | 0 | 0 | 0 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
(52) | Data Center 1 Solar PV - 30 MW | 0 | 0 | 0 | 0 | 0 | 0 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
(53) | Data Center 1 Wind - 30 MW | 0 | 0 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
(54) | Data Center 1 Wind - 50 MW | 0 | 0 | 0 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
(55) | Data Center 1 Wind - 50 MW | 0 | 0 | 0 | 0 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
(56) | Data Center 1 Wind - 50 MW | 0 | 0 | 0 | 0 | 0 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
(57) | 50 MW Solar PV for 2020 RPS | 0 | 0 | 0 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
(58) | 50 MW Wind for 2020 RPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(59) | Total Renewable Resources (MW) | 86.9311 | 109.2333 | 144.0356 | 186.3356 | 210.6378 | 242.2378 | 325.44 | 342.2422 | 376.6422 | 376.1444 | 410.6444 | 410.1467 | 399.8467 | 434.0489 | 468.3511 | 467.9511 | 467.5533 | 480.0533 | 479.5556 | 474.1556
(60) | Total System Resources (MW) | 2363.9311 | 2235.7333 | 2272.0356 | 2315.7356 | 2341.6378 | 2374.7378 | 2377.44 | 2395.7422 | 2431.6422 | 2432.6444 | 2468.6444 | 2505.1467 | 2535.8467 | 2570.0489 | 2604.3511 | 2630.9511 | 2817.5533 | 2830.0533 | 2829.5556 | 2824.1556
(61) | Reserve Margin (MW) | 493.3311 | 335.8333 | 346.0356 | 354.4356 | 342.2378 | 342.1378 | 324.74 | 324.9422 | 338.6422 | 318.8444 | 330.7444 | 337.2467 | 343.0467 | 345.3489 | 339.8511 | 327.3511 | 474.7533 | 449.5533 | 406.2556 | 355.7556
(62) | Reserve Margin (%) | 26.37% | 17.68% | 17.97% | 18.07% | 17.12% | 16.83% | 15.82% | 15.69% | 16.18% | 15.08% | 15.47% | 15.56% | 15.64% | 15.52% | 15.01% | 14.21% | 20.26% | 18.88% | 16.76% | 14.41%
Notes:
1. PNM assumes a capacity credit for renewable resources based on type of technology and contribution at the peak hour.
2. Demand response resources grossed up for transmission losses.
3. PNM assumes a 100% capacity credit for Prosperity Battery Demo
4. Capacity credit for geothermal resource is based upon developer estimates.